## Slide 1: Generating Sustained Oscillation
Increased u by h, (e.g., 5%)
After L, y increase, relay switches to opposite position,
As phase lag is -π, limit cycle a period Pu results.
H, height of the relay;
a, amplitude of oscillation.
Bring the system to steady-state
Repeat to generate sustained oscillation

## Slide 2: Ultimate Gain Analysis
Describing function for nonlinear system.
  only the first Fourier coefficient for frequency domain analysis.
For ideal relay, A1 = 0, B1 = 4h/π,
relay feedback oscillation frequency corresponds to limit of stability:
the ultimate gain (Ku) :

## Slide 3: Transfer function Modeling
Determine the model, back-calculation from gain and phase relation for parameters

## Slide 4: Example: Three Parameter Model
either L or Kp needed to solve for time constant, if L available, T, and Kp
Using gain and phase condition at ultimate frequency